## Instructions
Equation Calculator for LEED-NC v2.2 EAc40
Purpose
This calculation tool automatically solves the equations described in the USGBC document, LEED for New Construction Version 2.2. Use it to quickly determine whether the HVAC equipment-and-refrigerant combinations in a prospective LEED-NC project comply with the requirements of Energy & Atmosphere Credit 4.
How to use the calculator
NOTE: You may only enter values in turquoise-colored cells. All other entries either are calculated automatically or are fixed values.
1. Choose a worksheet by clicking the appropriate tab at the bottom of the Excel window. Pick the Single Unit worksheet to provide information for a single piece of equipment. Or, pick the Multiple Units worksheet to describe a project with different types of equipment and/or refrigerant.
2. Type the job name in cell B2.
3. Type the location of the job in cell B3.
4. OPTIONAL: Enter the appropriate unit tag(s) from the equipment schedule in cell(s) B5 through G5.
5. Enter the refrigerant type in cell(s) B6 through G6. Selecting the refrigerant type automatically inserts the appropriate GWP and ODP values from the LEED-NC v2.2 Reference Guide (EA Credit 4, Table 1) in rows 14 and 15, respectively.
6. Enter the equipment type in cell(s) B7 through G7. Selecting the equipment type automatically inserts the appropriate equipment life value(s) from the LEED-NC v2.2 Reference Guide in row 12.
7. For each refrigerant type and equipment type, enter the HVAC mechanical cooling capacity in cell(s) B8 through G8. If multiple units use the same refrigerant type, enter the sum of their capacities.
8. For each refrigerant type/equipment type combination, enter the HVAC refrigerant charge, in pounds, in cell(s) B9 through G9. If multiple units of the same equipment type use the same refrigerant type, enter the sum of their refrigerant charges in pounds.
The project qualifies for EA Credit 4 of LEED-NC v2.2 if the value in cell H21 (Multiple Unit worksheet) or C21 (Single Unit worksheet) is less than or equal to 100 and “Yes” is displayed in cell H22 or C22.
The project does not quality for this credit if the value in cell H21 (Multiple Unit worksheet) or C21 (Single Unit worksheet) is greater than 100 and “No” is displayed in cell H22 or C22.
7. OPTIONAL: To provide additional information about the project, type your comments in cell A87.
8. To print the caluclation results for your records and/or as documentation for your LEED project submittal, either click the Print button in the toolbar or open the File menu and select Print.
The report is automatically stamped with the date and time of the last calculation (cell B46).

## Single Unit
Equation Calculator for USGBC LEED-NC v2.2, Energy & Atmosphere Credit 4
Job name
Job location
Date and time of calculation | 2026-07-29 04:02
Unit tag(s) |  | All
Refrigerant type | R-123_Trane_Centrifugal | Qtotal
Equipment type | Centrifugal chiller
Capacity, tons (Qunit) | 0 | 0
Refrigerant charge, lb | 0
Refrigerant charge, lb/ton (Rc) | 0
Leak rate, % of charge per year (Lr) | 0.5%
Equipment life (Life) | 23
End-of-life refrigerant loss, % of charge (Mr) | 10%
Global warming potential of refrigerant (GWPr) | 76
Ozone depletion potential of refrigerant (ODPr) | 0.02
Life-cycle direct global warming potential (LCGWP) | 0
Life-cycle ozone depletion potential (LCODP) | 0
TSAC factor | 0
TSAC factor × capacity | 0 | 0
| Calculation | 100.1
| Credit? | No
Version 2.0 “Equation Calculator” for LEED-NC v2.2, EAc40 - July 2006
© 2006 American Standard Inc. All rights reserved
Trane, in providing this calculation tool, assumes no responsibility for the performance or desirability of any resulting system design. Design of the HVAC system is the prerogative and responsibility of the engineering professional.
LEED Energy and Atmosphere Credit 4 Submittal
LEED-NC v2.2 Calculation
Job name
Job location
Date | 2026-07-29 04:02
If only one type of refrigerant is used, the HVAC&R systems | do not comply with the formula:
OR
If multiple refrigerant types are used, the HVAC&R systems | do not comply with the formula:
RESULT
Using the appropriate equation, the final calculation equals | 100.1
Based on the LEED-NC v2.2 calculation for EA Credit 4, this project | does not qualify.
CALCULATIONS
Defaults used:
2% Leakage rate per year (Lr)
10% End-of-life loss of charge (Mr)
Equipment life varies by equipment type
ODP and GWP from LEED-NC v2.2 Reference Guide
Entered values:
R-123_Trane_Centrifugal
Unit tag(s)
Capacity, tons (Qunit) | 0
Refrigerant charge, lb | 0
Refrigerant charge, lb/ton (Rc) | 0
Global warming potential of refrigerant (GWPr) | 76
Ozone depletion potential of refrigerant (ODPr) | 0.02
LCGWP + 100,000 × LCODP | 0
Total capacity, tons | 0
Result: | 100.1
REMARKS
Note on A8: Capacity is a number. Using the space bar will generate an error. Please enter 0
Note on A9: Refrigerant charge is a number. Using the space bar will generate an error. Please enter 0
Note on A11: In 2006 leak rate data for Trane R-123 centrifugal chillers was submitted to the USGBC. A 0.5% annual leakage rate is approved for these chillers per a CIR published at www.usgbc.org
Note on B8: Capacity is a number. Using the space bar will generate an error. Please enter 0
Note on B9: Refrigerant charge is a number. Using the space bar will generate an error. Please enter 0
Orange = Fixed values
Turquoise = User entries
Yellow = Calculated values
Red = Ineligible result
Green = Eligible result
Red = Ineligible result

## Multiple Units
Equation Calculator for USGBC LEED-NC v2.2, Energy & Atmosphere Credit 4
Job name
Job location
Date and time of calculation | 2026-07-29 04:02
Unit tag(s) | [6 empty] | All
Refrigerant type | R-123_Trane_Centrifugal | R-134a | R-22 | Water | R-407c | R-410a | Qtotal
Equipment type | Centrifugal chiller | Screw chiller | Packaged AC or HP | Absorption chiller | Split-system AC or HP | Packaged AC or HP
Capacity, tons (Qunit) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigerant charge, lb | 0 | 0 | 0 | 0 | 0 | 0
Refrigerant charge, lb/ton (Rc) | 0 | 0 | 0 | 0 | 0 | 0
Leak rate, % of charge per year (Lr) | 0.5% | 2% | 2% | 2% | 2% | 2%
Equipment life (Life) | 23 | 23 | 15 | 23 | 15 | 15
End-of-life refrigerant loss, % of charge (Mr) | 10% | 10% | 10% | 10% | 10% | 10%
Global warming potential of refrigerant (GWPr) | 76 | 1320 | 1780 | 1890 | 1700 | 1890
Ozone depletion potential of refrigerant (ODPr) | 0.02 | 0 | 0.04 | 0 | 0 | 0
Life-cycle direct global warming potential (LCGWP) | 0 | 0 | 0 | 0 | 0 | 0
Life-cycle ozone depletion potential (LCODP) | 0 | 0 | 0 | 0 | 0 | 0
TSAC factor | 0 | 0 | 0 | 0 | 0 | 0
TSAC factor × capacity | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Weighted calculation | [5 empty] | 100.1
| Credit? | [5 empty] | No
Version 2.0 “Equation Calculator” for LEED-NC v2.2, EAc40 - July 2006
© 2006 American Standard Inc. All rights reserved
Trane, in providing this calculation tool, assumes no responsibility for the performance or desirability of any resulting system design. Design of the HVAC system is the prerogative and responsibility of the engineering professional.
LEED Energy and Atmosphere Credit 4 Submittal
LEED-NC v2.2 Calculation
Job name
Job location
Date | 2026-07-29 04:02
If only one type of refrigerant is used, the HVAC&R systems | do not comply with the formula:
OR
If multiple refrigerant types are used, the HVAC&R systems | do not comply with the formula:
RESULT
Using the appropriate equation, the final calculation equals | 100.1
Based on the LEED-NC v2.2 calculation for EA Credit 4, this project | does not qualify.
CALCULATIONS
Defaults used:
2% Leakage rate per year (Lr)
10% End-of-life loss of charge (Mr)
Equipment life varies by equipment type
ODP and GWP from LEED NC v2.2 Reference Guide
Entered values:
| R-123_Trane_Centrifugal | R-134a | R-22 | Water | R-407c | R-410a
Unit tag(s)
Capacity, tons (Qunit) | 0 | 0 | 0 | 0 | 0 | 0
Refrigerant charge, lb | 0 | 0 | 0 | 0 | 0 | 0
Refrigerant charge, lb/ton (Rc) | 0 | 0 | 0 | 0 | 0 | 0
Global warming potential of refrigerant (GWPr) | 76 | 1320 | 1780 | 1890 | 1700 | 1890
Ozone depletion potential of refrigerant (ODPr) | 0.02 | 0 | 0.04 | 0 | 0 | 0
LCGWP + 100,000 × LCODP | 0 | 0 | 0 | 0 | 0 | 0
Total capacity, tons | 0
Result: | 100.1
REMARKS
Note on A8: Capacity is a number. Using the space bar will generate an error. Please enter 0
Note on A9: Refrigerant charge is a number. Using the space bar will generate an error. Please enter 0
Note on A11: In 2006 leak rate data for Trane R-123 centrifugal chillers was submitted to the USGBC. A 0.5% annual leakage rate is approved for these chillers per a CIR published at www.usgbc.org
Note on B8: Capacity is a number. Using the space bar will generate an error. Please enter 0
Note on B9: Refrigerant charge is a number. Using the space bar will generate an error. Please enter 0
Note on C8: Capacity is a number. Using the space bar will generate an error. Please enter 0
Note on C9: Refrigerant charge is a number. Using the space bar will generate an error. Please enter 0
Note on D8: Capacity is a number. Using the space bar will generate an error. Please enter 0
Note on D9: Refrigerant charge is a number. Using the space bar will generate an error. Please enter 0
Note on E8: Capacity is a number. Using the space bar will generate an error. Please enter 0
Note on E9: Refrigerant charge is a number. Using the space bar will generate an error. Please enter 0
Note on F8: Capacity is a number. Using the space bar will generate an error. Please enter 0
Note on F9: Refrigerant charge is a number. Using the space bar will generate an error. Please enter 0
Note on G8: Capacity is a number. Using the space bar will generate an error. Please enter 0
Note on G9: Refrigerant charge is a number. Using the space bar will generate an error. Please enter 0
Orange = Fixed values
Turquoise = User entries
Yellow = Calculated values
Red = Ineligible result
Green = Eligible result

## Lists
Equipment type | Life
Absorption chiller | 23
Centrifugal chiller | 23
Packaged AC or HP | 15
Reciprocating chiller | 20
Screw chiller | 23
Split-system AC or HP | 15
Unitary AC or HP | 15
Window AC or HP | 10
Refrigerant type | GWPr | ODPr | Ann Lk % | EOL Loss %
Ammonia | 0 | 0 | 2% | 10%
Carbon dioxide | 1 | 0 | 2% | 10%
Propane | 3 | 0 | 2% | 10%
R-123 | 76 | 0.02 | 2% | 10%
R-123_Trane_Centrifugal | 76 | 0.02 | 0.5% | 10%
R-134a | 1320 | 0 | 2% | 10%
R-22 | 1780 | 0.04 | 2% | 10%
R-245fa | 1020 | 0 | 2% | 10%
R-404A | 3900 | 0 | 2% | 10%
R-407c | 1700 | 0 | 2% | 10%
R-410a | 1890 | 0 | 2% | 10%
R-507A | 3900 | 0 | 2% | 10%
Water | 0 | 0 | 2% | 10%